## FastHVAC-AixLib_simple
Typ | Component | NameTag | IFCElement | Needed parameters | Ifc Attribut / PropertySet | extended mapping
Component independent information | Flowdirection | FlowDirection |  | - | -
| Medium | Medium | IfcDistributionSystems | - | -
Generation | Boiler | Boiler | IfcBoiler | watervolume | Pset_BoilerTypeCommon/WaterStorageCapacity
|  |  |  | nominal power | - | Pset BoilerCommon: NominalEnergyConsumption + PartialLoadEfficiencyCurves
|  |  |  | min power | Pset_BoilerTypeCommon/NominalPartLoadRatio
|  |  |  | table efficiency as f(percentage power) | Pset_BoilerTypeCommon/PartialLoadEfficiencyCurves
| Combined heat and power unit | CHP | missing (IfcEnginge o. IfcUnitaryEquipment, only mechanical energy) | nominal power | -
|  |  |  | el. Efficiency | -
|  |  |  | fuel utilization rate | -
|  |  |  | type (ICE, PEMFC, SOFC …) | -
| Heatpump | HeatPump | missing (evtl. IfcUnitaryEquipment) | fluids (e.g. Water/Air) | -
|  |  |  | con. power as f(T_Sink & T_source) | -
|  |  |  | el. power as f(T_Sink & T_source) | -
|  |  |  | limits for T_sink | -
|  |  |  | nom. massflow in Eva & Con | -
|  |  |  | volumes of Eva & Con | -
| Chillers | Chiller | IfcChiller | fluids (e.g. Water/Air) | IfcChillerType
|  |  |  | coolingpower as f(T_Sink & T_source) | Pset_ChillerTypeCommon/CapacityCurve
|  |  |  | el. power as f(T_Sink & T_source) | - | Pset_ChillerTypeCommon: CapacityCurve + CoefficientOfPerformanceCurve
|  |  |  | partload efficiencies | Pset_ChillerTypeCommon/FullLoadRatioCurve
|  |  |  | volumes of Eva & Con | -
Storage | Storages | Storage | IfcTank | storagetype | Pset_TankTypeCommon/StorageType
|  |  |  | height | Pset_TankTypeCommon/NominalLengthOrDiameter
|  |  |  | diameter | Pset_TankTypeCommon/NominalWidthOrDiameter
|  |  |  | position of ports | - | geometric determination
Distribution - Hydraulic | Pumps | Pump | IfcPump | - | -
| Valves | Valve | IfcValve | - | -
| Pipes and connectors | Pipe | IfcPipeSegment u. IfcPipeFitting | outer diameter | Pset_pipesegmenttypecommon/OuterDiameter
|  |  |  | inside diameter | Pset_pipesegmenttypecommon/InnerDiameter
|  |  |  | length | - | geometric determination via port distances
|  |  |  | insulation thickness | - | -
| Heattransfer (simple) | SpaceHeater_Simple | - | - | - | -
| Heattransfer (physical) - Radiator) | SpaceHeater_Radiator | IfcSpaceHeater | type (number of surfaces) | Pset_spaceheatertypecommon/NumberOfPanels | -
|  |  |  | surface area | - | geometric determination
|  |  |  | nominal power [W/m] | Pset_spaceheatertypecommon/OutputCapacity | -
|  |  |  | radiator exponent | - | -
|  |  |  | watervolume | - | estimation by geometry
|  |  |  | radiator mass | pset_spaceheatertypecommon/BodyMass | -
|  |  |  | radiator material | - | Pset_spaceheatertypecommon/ThermalMassHeatCapacity / pset_spaceheatertypecommon/BodyMass
| Heattransfer (physical) - underfloor heating | SpaceHeater_Underfloow | IfcSpaceHeater | pipediamter | - | geometric determination
|  |  |  | pipelength | - | geometric determination
|  |  |  | depth of instalation | - | geometric determination